# Using Modems with

# dataTaker DT800 Data Loggers

(Multithread Firmware >Version 2 Build 41 and later)

## Contents

1. Introduction	2

2. Modem Control Commands	2

2.1  INSTALLMODEM	2

2.2  UNINSTALLMODEM	3

2.3  SETDIALOUTNUMBER	3

2.4  DIAL	3

2.5  HANGUP	3

2.6  Example of Modem Command Usage	4

3. Modem Control Settings	4

4. The Modem Machine State	5

5. Example Program	6

6. Installing a Modem	6

6.1  Modem Cable	6

6.2  Modem Setup	7

6.3  DT800 Setup	8

6.4  DeTransfer Timeout	8

6.5  Completing the Installation	9

7. Operation of the Link	9

8. Visits to Site	9

9. Trouble Shooting	9

## 1. Introduction

The dataTaker DT800 data logger has a communications mode which facilitates the use of modems with the loggers. This modem communications mode provides both dial-in and dial-out functions, and can be used with both PSTN (landline) and GSM (cellular) modems.

It is not mandatory to use this mode to communicate with the DT800 via modems, however this mode simplifies and stabilises this form of communication.

This document describes the modem support functionality for the multithread version of the dataTaker DT800 firmware, version 2 build 41 and later (the version and build of the firmware in your DT800 can be determined by the TEST0 command).

In this document the following conventions are used

installed modem	- a modem that is physically connected to the DT800 serial host port, 
  but is not enabled for communications

connected modem	- a modem that is physically connected to the DT800 serial host port,
  and is enabled for communications by successfully dialling out or
  answering an incoming call

## 2. Modem Control Commands

The following Modem Control Commands support the modem communications mode of the dataTaker DT800 data loggers:

2.1 INSTALLMODEM

This command switches the DT800 from the direct RS232 communications mode to the modem communications mode. The INSTALLMODEM command is entered via a direct RS232 connection, or via an ethernet connection, and once entered then direct RS232 communications with the logger are disabled until the logger is switched back to the direct RS232 communications mode.

The modem communications mode can also defined as part of the user profile of the logger, by the commands

PROFILE”HOST_PORT”,”MODEM_INSTALLED”=”YES”

where the DT800 will always initialize in the modem communications mode following a SINGLEPUSH or triple push reset, and

PROFILE”HOST_PORT”,”MODEM_INSTALLED”=”CHECK”

where the DT800 will check if a modem is connected following a SINGLEPUSH or triple push reset, and initialize in the modem communications mode if a modem is found otherwise will initialize in the direct RS232 communications mode.

When the modem communications mode is first entered, the DT800 then proceeds as follows:

- the DT800 begins to monitor the RS232 host port for the presence of an installed modem, and starts issuing the modem reset command +++ATZ every minute and looks for an OK response from the modem

- if an OK response is returned by the modem, then the presence of a modem is confirmed and the DT800 is ready for making and answering calls.

- after the presence of an installed modem is confirmed, the DT800 then continuously monitors the modem to detect possible disconnection. The DT800 issues the modem attention command AT to the modem every minute, and looks for an OK response from the modem. If the modem ever fails to respond to the AT command, the DT800 then begins to issue the modem reset command again to attempt to recover the modem

The modem reset command for your particular modem can be defined in the DT800 if the default +++ATZ is not appropriate (see Modem Control Strings below).

While the DT800 is in the modem communications mode, but not connected to an installed modem, then all commands sent to the logger are ignored. This includes commands sent via a direct RS232 connection from a computer, and any stray text strings issued by an installed modem while powering up, powering down or establishing a connection. Commands are only accepted by the logger while there is a modem communications session established. However any commands sent to the logger via the ethernet port are always accepted by the logger, regardless of the current state of the modem communications mode.

Similarly, while the DT800 is in the modem communications mode but not connected to an installed modem, the logger does not transmit any realtime data, alarms messages, error messages, etc.

Response by the DT800 to the various reset functions while in the modem communications mode is as follows:

- if the DT800 is reset by the RESET command while in the modem communications mode, it will remain in the modem communications mode

- if the DT800 is reset by the SINGLEPUSH command, or is given a single push or triple push reset, while in the modem communications mode, it will initialize according to the setting of PROFILE”HOST_PORT”,”MODEM_INSTALLED” in the user profile

2.2 UNINSTALLMODEM

This command switches the logger back to the direct RS232 communications mode. The command must be issued either through the modem connection, or through an ethernet connection.

The DT800 can also be switched back to direct RS232 communications mode by sending the ASCII Delete character DEL into the RS232 host port of the logger at the baud rate of 57600 baud.  A practical way of doing this is to connect to the logger with DeTransfer, using either an autobauding connection with hardware flow control enabled, or a connection fixed at 57600 baud with hardware flow control enabled. The mechanism is such that DeTransfer will fail the first attempt to connect, but will connect with the logger on the second attempt.

If the user profile contains the setting

PROFILE”HOST_PORT”,”MODEM_INSTALLED”=”NO”

or there is no definition for PROFILE”HOST_PORT”,”MODEM_INSTALLED” in the user profile, then the DT800 will revert to the direct RS232 communications mode following a SINGLEPUSH command or a single push or triple push reset.

2.3 SETDIALOUTNUMBER

Specifies the telephone number to be dialled to establish a dial-out connection.

The number must include any prefixes such as country codes, area codes, etc. necessary to reach the required number.

2.4 DIAL

Dials out and connects to the telephone number specified by SETDIALOUTNUMBER. If a call cannot be placed for any reason, then the command is ignored.

2.5 HANGUP

Hangs up or disconnects the current dial-out or dial-in connection. If there is currently no connection, or the command is issued in direct RS232 communications mode, then the command is ignored.

2.6 Example of Modem Command Usage

The use of these modem control commands is demonstrated in the following example program which is entered into the data logger during a direct RS232 connection:

BEGIN

SETDIALOUTNUMBER"12345678"

RA10M

‘Read boiler temperature

1TK(=1CV,W)

IF(1CV>120){[DIAL]”High Temperature^M^J”}

END

INSTALLMODEM

The program will cause the data logger to dial-out to phone number 12345678  every 10 minutes if the temperature is greater than 120 DegC, after a modem is connected to the host port. It is presumed that the location receiving the dial-out hangs up the connection each time.

## 3. Modem Control Settings

The DT800 uses a number of modem control strings and timeouts to manage an installed modem.

The DT800 has default settings for these control strings and timeouts, however if your modem or application requires different modem control strings and/or timeouts then alternatives can be defined.

Alternative modem control strings and timeouts are stored in the user profile by the command

PROFILE”HOST_MODEM”,”ModemControlSetting”=”Setting”

where “ModemControlSetting” is the particular control string being set, and “Setting” is the actual modem control string required for your modem.

The modem control strings and timeouts are detailed in the table below, including the default for each

| Modem Control Setting | Legal Values | Default Setting |
| --- | --- | --- |
| DIAL | string | ATD |
| HANGUP | string | ATH0 |
| ANSWER | string | ATA |
| RESET | string | ATZ |
| RESPONSE | string | OK |
| ATTENTION | string | AT |
| END_DATA_MODE | string | +++ |
| RING | string | RING |
| CONNECT | string | CONNECT |
| COMMAND_DELAY | number>=0 | 3 |
| INIT_REPETITION_PERIOD | number>=0 | 60 |
| COMMAND_ANSWER_TIMEOUT | number>=0 | 5 |
| DIAL_TIMEOUT | number>=0 | 60 |
| ANSWER_TIMEOUT | number>=0 | 30 |
| ESCAPE_BEFORE_HANGUP | NO | NO |
|  | YES |  |

The default modem control strings and timeouts will be suitable for most modems. However for some modems the RESET string may need to be changed to “ATZ0” (check your modem manual for details), and the RESPONSE string may need to be changed for modems which respond in other languages or have numeric response codes.

If you wish to restore the default setting for a modem control string or timeout, then you must enter the

PROFILE”HOST_MODEM”,”ModemControlSetting”=”Default”

command and explicitly set the particular modem control string or timeout to its default setting shown in the table above.

These alternative settings for modem control strings and timeouts are available following powerup, following a SINGLEPUSH command, and following a single push or triple push reset. Alternative settings for modem control strings and timeouts are maintained through a RESET command.

The following program shows change to modem control string and timeout settings

PROFILE”HOST_MODEM”,”RESET”=”ATZ0”

PROFILE”HOST_MODEM”,”ANSWER_TIMEOUT”=”45”

BEGIN

SETDIALOUTNUMBER"12345678"

RA10M

‘Read boiler temp

1TK(=1CV,W)

IF(1CV>120){[DIAL]”High Temperature^M^J”}

END

INSTALLMODEM

Note that the PROFILE commands to define the RESET string and the ANSWER_TIMEOUT only need to be entered once, and are maintained in the user profile until changed again. They do not need to be part of every program sent to the logger which uses the particular modem to which the settings pertain.

4. The Modem Machine State

The state of the internal modem machine which manages the installed modem can be accessed via the System Variable 25 (25SV).

The value of 25SV indicates the current state of the modem machine, and is detailed below:

| 25SV | Description |
| --- | --- |
| 0 | Unknown modem state |
| 1 | No modem installed (direct RS232 connection) |
| 2 | Modem installed, but not successfully initialized |
| 3 | Modem in command mode, ready to receive dial and answer commands |
| 4 | Modem is connected, comms now possible in both directions |
| 5 | Temporary; modem is currently dialing out |
| 6 | Temporary; modem is currently answering an incoming call |
| 7 | Temporary; modem is initializing - Stage 1 |
| 8 | - Stage 2 |
| 9 | Temporary; modem is hanging up - Stage 1 |
| 10 | - Stage 2 |
| 11 | - Stage 3 |
| 12 | Temporary; DT800 is checking for presence of a modem |

The value of 25SV at any time indicates the current state of the installed modem. This information can be used in various ways by the user program, such as

- managing the modem around switching the modem's power supply to save site battery

- synchronising message transmission with dial-out delay, etc

- automatically re-install a modem after direct connection (eg. with DeTransfer)

The temporary modem states indicated by 25SV values of 5, 6, 7, 8, 9, 10, 11 and 12 can be brief, and generally should not be used in programs. These states are primarily for debugging purposes.

5. Example Program

The following program example demonstrates the use of some of the modem control commands, modem control settings, and the state of the modem machine to sequence the transmission of an alarm message to a central computer

‘User profile settings entered once

PROFILE”HOST_PORT”,”MODEM_INSTALLED”=”CHECK”

PROFILE”HOST_MODEM”,”RESET”=”ATZ0”

PROFILE”HOST_MODEM”,”ANSWER_TIMEOUT”=”45”

‘The program

BEGIN"TEST1"

SETDIALOUTNUMBER"97648943"

'Alarm message

1$="THIS IS AN ALARM MESSAGE"

'Site ID

4$="Pump 37"

'Alarm true flag

98CV(W)=0

'Alarm false flag

99CV(W)=0

RA5S

'Look if input is in alarm state, if so toggle flags and DIAL

ALARM1(3TK>45){[98CV(W)=1 99CV(W)=0 DIAL]}

'Look if any DIAL was successful, if so send the alarm message

IF(98CV>0)AND

IF(25SV><3.9,4.1){[1$(NL)]}

'Look if channel is not in alarm state, if so toggle flags

ALARM2(3TK<45){[98CV(W)=0 99CV(W)=1]}

'Look if alarm has cleared while in DIAL state, if so HANGUP

IF(99CV>0.5)AND

IF(25SV><3.9,4.1){[HANGUP]}

END

6. Installing a Modem

Installing a modem onto the RS232 host port of the DT800 for the modem communications mode requires the following steps.

6.1 Modem Cable

Modems are usually supplied with a communications cable for connecting the modem to a computer COM port. The cable may have a 25 pin D connector and a 9 pin D connector at the computer end, or just a 9 pin D connector at the computer end.

This cable is used to connect the modem to your computer to initially configure the modem (see below), and then used to connect the modem to the DT800.

Some modems are supplied without a cable, particularly GSM modems. If your modem does not have a cable then consult your modem supplier for a PC compatible cable, making sure that Rx, Tx, Gnd, DCD, RTS, CTS and RI lines are provided in the cable. Note that DB25 to DB9 adaptors often don’t have the RI line connected through, and so would prevent the DT800 from receiving incoming calls.

Siemens M20 - If you are using a Siemens M20 GSM modem, then a 9 pin ‘straight through’ cable is required.

Wavecom WM02 - If you are using a Wavecom WM02 GSM modem, then you will have to configure a cable as follows

PC/DT800                             Wavecom WM02

(DTE)                                 (DCE)

9 pin D                               15 pin D

DCD  1  ----------------------------  1  DCD

Rx  2  ----------------------------  6  Rx

Tx  3  ----------------------------  2  Tx

SG  5  ----------------------------  9  SG

RTS  7  ---------------------------- 12  RTS

CTS  8  ---------------------------- 11  CTS

RI  9  ---------------------------- 13  RI

6.2 Modem Setup

There are minimum requirements for the configuration of the installed modem. These requirements apply to both PSTN (landline) and GSM (cellular) modems, however the commands to achieve the settings may differ for particular modems. Consult the users manual for your modem (it may be supplied as a .pdf file on the CD supplied with your modem, otherwise contact your modem supplier).

Connect your modem to your computer as described in your modem users manual, and configure your modem as follows using either DeTransfer or Windows HyperTerminal.

- the modem should first be set to the factory default configuration by the command

AT&F   or   AT&F0

- the modem RS232 port must be capable of communicating with the DT800 at 57600 baud.

Set the modem to autobaud if available, or fix the baud rate to 57600 baud by command. The command will vary between modems, for example for modern PSTN modems the RS232 port is autobauding by default and does not need to be set. Alternatively it may be necessary to fix the baud rate with a command similar to

	AT+IPR:0		autobauding
	AT+IPR:57600		fixed at 57600 baud

GMS modems tend not to be autobauding to higher baud rates. To set the baud rate of a GSM modem, the command is similar to

	AT+IPR=57600

- Modern modems default to hardware (RTS/CTS) handshake on their RS232 port, which should be left enabled. If this is disabled by default in your modem, then enable hardware handshake by the appropriate command.

- The DT800 always supports software (XON/XOFF) flow control in the modem communications mode, both when hardware handshake is enabled or disabled.

If software handshake can also be selected in your modem, then it may be an advantage to enable it in pass through mode if possible. The command might be similar to

AT+IFC=3,1

Don’t enable local software handshake between your modem and the calling modem.

- Make sure that the default profile for your modem has command echo enabled (ATE1), result codes enabled (ATQ0)  and autoanswer disabled (S0=0). These settings are usually all defaults, however can be checked by the AT&V command to view the configuration profile.

- When the modem has been configured, save the configuration in the users profile by the command

	AT&W    or    AT&W0

This profile will be loaded in future whenever the modem is repowered, and whenever the modem executes a +++ATZ or ATZ command.

- Siemens M20 - If you are using a Siemens M20 GSM modem, then the configuration is

	AT&F
	AT+IPR=57600
	AT+IFC=3,1
	AT&W0

- Wavecom WM02 - If you are using a Wavecom WM02 GSM modem, then the configuration is

	AT&F
	AT+IPR=57600
	AT&W

- If you are using a new modem that you are not fully familiar with, then it is recommended that you check its suitability by following the test procedure described in the Trouble Shooting section below.

6.3 DT800 Setup

The DT800 must be configured as follows

- It is recommended that you set the RS232 host port parameters of the DT800 by the command 

	PH=57600,N,8,1,HWFC

Other settings will work, however these will add considerable difficulty to the procedures.

- the DT800 program for the application could be entered at this time

- finally set the DT800 into the modem communications mode by issuing the command

	INSTALLMODEM

This must be the last command issued, because after this command is executed then direct communications with the logger will no longer be possible.

6.4 DeTransfer Timeout

When DeTransfer is connecting to a DT800, or communicating with a DT800, there is a timeout within which the DT800 must respond to commands sent by DeTransfer.

However when DeTransfer is connecting to a remote DT800 via a modem link, this timeout can be exceeded if the network is busy, if the network has long latencys, if there is line noise causing retries, etc. and so the connection will fail. It will appear as if the modem or DT800 has hung.

If you are connecting to your DT800 via PSTN or GSM networks, then it is strongly recommended that you extend this timeout as follows

- from the Start Menu of Windows select Run

- enter REGEDIT into the input field of the Run dialog box, and click OK

- REGEDIT will run and display a folder list

- navigate through HKEY_CURRENT_USER|Software|dataTaker and click on the DeTransfer folder to open it

- double click on Extended Delay, and change its value from 0 to the number of milliseconds that you wish to extend the delay, for example 2000 extends timeout by 2 seconds.

- click OK

- close REGEDIT

- close DeTransfer (if running) and restart DeTransfer to load in the new setting

6.5 Completing the Installation

When the modem, the DT800 and DeTransfer have been configured, connect the modem cable to the RS232 host port of the DT800.

The DT800 will begin to test for the presence of an installed modem within a minute, and when a modem is found will initialise the system to send and receive calls. You should not attempt to dial into the DT800/modem site until after this initialisation has been completed – allow say 2-3 minutes.

(Periodic testing by the DT800 for an installed modem can be seen by connecting an eavesdrop between the DT800 and the modem.)

7. Operation of the Link

Once initialisation is complete, you can dial into the site from a central PC and local (internal) modem to program the logger, recover data, change program variables, etc. as appropriate. If you are running DeTransfer or DeLogger 4 on your central PC, then install your local modem into Windows using the Modem Installer in the Windows Control Panel, and access this from within DeTransfer or DeLogger 4 connections properties.

Programming of the logger can also be done when configuring the logger.

8. Visits to Site

If you visit the site where the DT800/modem are installed, then you can communicate directly with the DT800 from your PC/Notebook by the following procedure

- disconnect the modem cable from the DT800

- connect your PC/Notebook to the DT800 using the cable supplied with the logger

- run DeTransfer, and use a connection defined as COM 1 or 2, 57600 baud, No parity, 8 data bits, 1 stop bit, hardware flow control to connect to the logger

- the first attempt to connect to the logger will fail - this process cancels the INSTALLMODEM state in the logger

- the second attempt to connect to the logger should succeed

- proceed with your local DeTransfer / DT800 session

- before disconnecting DeTransfer from the logger, send the INSTALLMODEM command as the last command

- disconnect DeTransfer

- disconnect the PC/Notebook cable from the DT800

- reconnect the modem cable to the DT800

9. Trouble Shooting

If you are having trouble getting a modem to function in the DT800 modem communications mode, then the following the procedure may help locate and remedy the problem

- Connect the modem to your PC with the cable supplied, then run DeTransfer and connect to the modem using a Generic connection of COM 1 or 2, 57600 baud, No parity, 8 data bits, 1 stop bit, hardware flow control. Consult your modem manual if you are having difficulties doing this.

- If DeTransfer cannot connect to the modem

- the modem may not be autobauding on its RS232 port. Check your modem manual for setting the baud rate of the modem RS232 port. It may be necessary to connect to the modem at a lower baud rate, issue a command to switch the modem RS232 port to 57600 baud, then reconnect at the 57600 baud rate

- the RTS and CTS lines of the DT800 and modem may not be connected through the cable and/or any adaptors used. Check and remedy if necessary.

- When the modem has connected to DeTransfer at 57600 baud, send the AT&F command to load the factory default profile for the modem. Be aware that this may set the modem RS232 port baud rate back to a default other than 57600 baud!!

- Send +++ATZ command, which is the default modem reset string in DT800. The modem should echo the command and respond OK

If not

- Make sure that return of response codes is enabled by ATQ0 command, and retry

- Send ATZ reset command. If the modem now responds with “OK” then use this command in future to reset the modem. Change the DT800 user profile accordingly with the command

	PROFILE”HOST_MODEM”,”RESET”=”ATZ”

- If the modem responds with something other than “OK”, such as in a different language, but otherwise appears to be functioning correctly, then declare this response in the user profile by the command

	PROFILE”HOST_MODEM”,”RESPONSE”=”string”

to ensure that the DT800 can recognize this alternative response.

- Send an AT command. The modem should respond with OK (or whatever is declared in the user profile for ”HOST_MODEM”,”RESPONSE”)

- Send ATDphonenumber command. The modem should dial and connect to a remote modem. On connection, the DCD (pin 1 on DB9) line should change polarity. Check that this line is connected through the cable and any adaptor to be used to connect the modem to the DT800.

If a different dial prefix is required (see your modem manual), then declare it in the user profile by the command

	PROFILE”HOST_MODEM”,”DIAL”=”string”

for all future programs.

- Send +++ATH0 command. This is the default hang-up command. The modem should disconnect from the remote modem and go on-hook.

If the modem does not hang up, then consult the modem manual for
  - other command formats, and declare in the user profile by the command

		PROFILE”HOST_MODEM”,”HANGUP”=”string”

     in all future programs

  - some modems require a delay between +++ and ATH0, and declare in the user profile by the command

		PROFILE”HOST_MODEM”,”COMMAND_DELAY”=”delay_in_secs”

     in all future programs

If the modem does not hang up in response to this command, then the HANGUP command of the DT800 cannot be used. However the modem can still be hung up from the other end.

- Dial from the other end to the test modem. While test modem is ringing make sure that the RI line (pin 9 on DB9) changes polarity. Make sure that this line is connected through in all of the cables and adaptors to be used with the logger. In all DB25 to DB 9 adaptors we have tested, the RI line was not connected through.

- While the test modem is ringing, send it the ATA command . The test modem should pick up the line and connect, issue a connect response, and DCD line (pin 1 of DB9) should change polarity.

- Remember to send INSTALLMODEM command to the DT800 before connecting the modem to the DT800.

The above procedure checks all the modem functions required to work with the DT800.